## Slide 1: Renewable Sources of Electricity for Penn State University Park
Osahon Abbe & Olaide Oyetayo,

## Slide 2: University Park Electricity Consumption
Annual Electricity Consumption in UP is
320, 000MWh
10.7 percent of the electricity from wind energy
5.2 percent of the electricity comes from biomass
Penn State currently has contracts with three companies to supply green power.
http://energy.opp.psu.edu/energy-programs/procurement/green-power/green-power

## Slide 3: Problem Statement
A comparison of biomass and wind energy as potential alternative source of electricity for Penn State University Park, and the techno-economic feasibility analysis of the chosen option for implementation on the campus.

## Slide 4: OBJECTIVES
Explore two renewable sources of electricity for University Park Campus.
Detailed comparison of Biomass and Wind Energy
  Resource Availability in Pennsylvania
    Optimal wind speed to generate power vs PA wind speed
    Annual Biomass Resource in PA
  Efficiency/Cost

## Slide 5
http://www.energy.ca.gov/biomass/index.html
http://www.greenwindsolar.com/about_wind_energy.php
Burning Biomass produces steam which generates electricity
Electricity generated from turbines powered by the wind

## Slide 6: Wind Energy
Unequal solar heating produces wind
Wind creates a lift that spins the turbine blades and rotor
Kinetic energy in wind is converted to mechanical energy in the turbine which is then converted into electrical energy in a generator.

## Slide 7: Wind Energy
Power in the wind
  P=1/2*ρAV3
    ρ : density of air (Kg/m3)
    A: swept rotor area (m2)
    V: wind speed (m/s)
    P: Power (watts)
Efficiency
  Governed by Betz’s Law: proscribes turbine max efficiency (59.3%)
  Turbine efficiency range between 25-45 percent

## Slide 8: Wind Energy
Wind Speed
  Cut-in speed: minimum speed needed for a wind turbine to generate “usable” power (7-10mph).
  Rated speed: minimum speed needed for a wind turbine to generate designated rated power (25-35mph).
  Energy generated increases by a cube of wind speed.
    E.g. doubling wind speed increases energy by a factor of eight (23=8)
  14 mph needed to generate enough electricity that is competitive with coal-fired.
  This will be used as a guide to determine whether there is enough wind in PA for our purpose.

## Slide 9: Wind Power Growth
Federal wind production tax credit (PTC) incentive
Environmental concerns
Improvements in wind energy technology
  Turbines are 100 time powerful than in the 80s
  More competitive because cost declined
  More investments
  Government incentives

## Slide 10: Types of wind turbines over the years…

## Slide 11: Wind Power Growth
GE 2.5MW Wind Turbine Series evolution.

## Slide 12: Wind Turbines
Design Variables
  Rotor Diameter
  Generator Capacity
  Hub height
  Rotor blade Design

## Slide 13: Advantages
No direct emissions of pollutants (SOx , NOx , CO2, mercury)
Facilitates rural development-farmers receive royalty payment for use of their lands.
Green jobs
Does not require water for operation

## Slide 14: Disadvantages
High dependency on wind consistency
Deaths of birds and bats
Need for new transmission infrastructure
“Eye sore” to some
Storage is expensive and still under development
Noise pollution

## Slide 15: Biomass
Solar energy stored in chemical bonds of organic materials
Renewable since we can grow more
The chemical energy is released as heat when biomass is burned.

## Slide 16: Biomass Types
Type | Energy Content (Btu/lb)
Dry Wood | 7600-9600
Wood (20% moisture) | 6400
Agricultural Residue | 4300-7300
Sludge Wood | 5000
Municipal Solid Waste | 5000
Landfill Gas | 250

## Slide 17: Biomass Conversion
Combustion: Burning of biomass to create steam which is converted to electrical energy by steam turbines
Gasification: Heating biomass in an oxygen-starved environment to produce gases (CO and H2). These gases have higher combustion efficiencies.
Co-firing: Combustion of two different fuels at a time. Usually biomass is fired with coal to reduce emissions.
Cogeneration: Simultaneous production of electricity and heat from a single fuel.

## Slide 18: Advantages
Comes from renewable sources
Reduces dependency on fossil fuels
Reduction of waste that end up in landfills
Can generate electricity at any time.
Little to no net gain of atmospheric CO2

## Slide 19: Disadvantages
Some biomass plants have relatively high NOx emission rate compared to other combustion technologies.
High CO emission compared to coal plants
Particulate Emissions (no biomass facilities currently have advanced particulate emissions control)
Environmental impact of collection, transportation, and processing.

## Slide 20
Resource availability in centre county

## Slide 22
State Game Lands (yellow)
State Forest (Green)
Areas that cannot be developed:
Federal lands
State Lands
Airfields, urban, wetland and water areas.
3 km surrounding
those areas
(1.864mile)

## Slide 23: Sandy Ridge Wind Farm
Approval of this project suggests no disturbance found
Approval of other wind projects is viable if land is appropriate.
Company did not develop in areas with highest wind speed
  Also stated has “reached a peak in identifying potential locations for wind turbine projects”

## Slide 24
The best wind speed is around the Phillipsburg area. (~6m/s)
Power in the Wind in this area is not sufficient

## Slide 25: Biomass Resource in Centre County
Source | Amount (thousand dry tonnes/yr) | Electricity Generation (potential, thousand MWh)
Primary Mill Residue (wood and bark from manufacturing plants) | 10-25 | 49-155
Secondary Mill Residue (sawdust, wood scraps) | 500-1000 tons/yr | 2 -6
Forest Residue | 25-50 | 123-310
Crop Residue | 20-50 | 55-235
Municipal Waste | 100,000 tons/yr | 194
Urban wood waste | 10-25 | 49-155
Methane emissions from domestic water treatment | 100-250 | 16-40

## Slide 26
BIOMASS

## Slide 28: Show Stoppers
Sustainability
Environmental impact of biomass transport
Economics
  Capital Cost
  Cost of fuel/transportation
  Price of electricity
    ≤10¢/kWh
    For comparison with levelized cost of generating electricity
Permits/Regulations

## Slide 29
  DESIGN &
  ECONOMICS

## Slide 30: Fuel Requirements
10MW capacity, 85% Capacity Factor.
Assumed 40% efficiency
Calculated 50000 tons/year.

## Slide 31: Procurement
Wood pellets acquired within 50 miles of state college preferred.
Energex American Inc. Mifflintown, PA
  120,000 tons per year
  45 miles from SC
  Price/Availability

## Slide 32: Location, Supply, and Handling
Location
  Locate plant next to existing generating plant
  Share electrical substation
Supply
  Energex (<50 miles from SC)
  Biomass delivered at $150/short ton
Handling
  Wood storage designed to hold 3-week supply of biomass.
  Biomass drying is unnecessary; pellets have 5 percent moisture content

## Slide 33
Circulating Fluidized Bed Gasifier.
Dimensions
  Height: 14.8 m
  Diameter: 2.07 m
Primary Oxidant
  Oxygen
Secondary Oxidant
  Air
  To increase the temperature in gasifier
Conditions
  10000C
  18 bar
Circulating and Stationary Material
  Silica sand
  20-30 wt. % calcinated dolomite

## Slide 34: Air Separator
Using oxygen prevents the dilution of fuel gas with nitrogen
Reduces formation of NOx
Produces Medium heating value gas rather than low heating value

## Slide 35: Gas Clean-up
Gas Cooling
  Direct Injection of water to reduce gas temperature to 500C and condense alkali species.
  Dilutes fuel gas but simplest and least expensive method.
  Reduces NOx formation in combustor
Hot Candle Filter
  Removes particulates
  Deposits solids on the side of the candle.

## Slide 36: CO2 Capture
Separation of CO2 from fuel gas
Impact on System Performance
  Avoided CO2 in the atmosphere: 0.14Kg/KwH (10424Kg)
  Decreases efficiency by six percent
  Increases capital cost by 38%
  Increases O&M cost by 31%

## Slide 37: Water Supply
Like PSU steam plant, use borough water as well as campus water.
Water Treatment
  Water contains 550 ppm TDS and 350 ppm hardness
  Softened to remove Ca & Mg; Demineralized
IGCC uses approximately 360-540 gallons/MwH
~27-40 million gallons/year

## Slide 38: Other Considerations
Waste management
Environmental
Energy Balance
Economics

## Slide 39: Financial Model for Feasibility study
Startup Costs
  Financing Costs
  Permits and Construction
  Physical Plant and Equipment
  Management
Operating Costs
  Fuel, water, other consumables
  Ash disposal
  Equipment maintenance
  Payroll
  Taxes and Insurance
Financial Events
  Changes in fuel supply cost
  Changes in power contract
  Refinancing
  Changes in regulatory environment

## Slide 40: Know the following:
  Available quantity of fuel and long term contract to purchase
  Quoted power system electricity price
  Financing to cover plant construction, equipment purchases, startup expenses
  Financial model for business for about 20 to 30 years

## Slide 41: Some inputs into Financial Model
Type and size of plant (10MW)
Cost of plant equipment and construction
Operating costs
Operating efficiency, actual power produced
Inflation rate for important costs

## Slide 42: Sensitivity Analysis
Disruptions in fuel supply, quantity and quality
Technology choice: capital costs, operating costs, efficiency, operating performance and reliability
Power contract terms
Financing terms
Subsidies
Ownership Structures

## Slide 43: Also considered…
Tax schedule
Depreciation schedule based on government incentives

## Slide 44: Conversion Technology-BIGCC
Secondary oxidant
Biomass

## Slide 45: Air Separation Unit (Revisited)
Avoids nitrogen dilution of the fuel gas
Increases heating value of gas
Increases cold gas efficiency
10 MW plant is small
Integration of ASU in small plant is not a good investment
Air is the oxidant

## Slide 46: CO2 Capture
Separation of CO2 from fuel gas
Impact on System Performance
  Avoided CO2 in the atmosphere: 0.14Kg/KwH (10424Kg)
  Decreases efficiency by six percent
  Increases capital cost by 38%
  Increases O&M cost by 31%

## Slide 47: Safety & Environmental
Biomass Absorbs about 890g CO2/ kWh
BIGCC power plants releases 890g CO2/kWh
Biomass Production
Transportation
Construction
Fossil Energy consumed: 231KJ/kwh
4049 g/kWh

## Slide 48
231 MJ/MwH Consumed
3600MJ/MwH
Energy Ratio=3600/231=15.6

## Slide 49: Act 213
This act ensures that all qualified alternative energy sources meet all applicable environmental standards and shall verify that an alternative energy source meets the standards
  Permits (Federal and State)
  Compliance (Violations)

## Slide 50: Permits
Major Permits for New Construction
  PSU NPDES – National Pollutant Discharge Elimination System
  PCSM- Post Construction Storm-water Management

## Slide 51: Compliance
Air Pollution
Ambient Air Quality (EPA 40CFR 81.339)
Environmental Control Definition
Good Engineering Practice Stack height
Water pollution
Waste Management
Noise
Boiler and Pressure Vessels
Archeological, Historic and Cultural resources
Emergency Management Procedure
Flood Hazards Review
Well Drilling for Monitoring
Asbestos Abatement
Zoning

## Slide 52: Discharges to wastewater systems should not exceed…
Substance | Concentration (mg/l)
Arsenic | 0.1
Cadmium | 0.07
Chromium | 0.2
Copper | 0.005
Lead | 0.1
Mercury | 0.02
Silver | 3.0
Zinc | 0.08
Cyanide | 0.1
Nickel | 0.25

## Slide 53: Emission limits in US clear skies
Pollutant | Emission limit
Sulfur dioxide | 2.0 lb/MwH
Nitrogen oxides | 1.0 lb/Mwh
Particulate Matter | 0.2 lb/MwH
Mercury | 0.015 lb/GWh
Notes: Gasification Chapter 9 page 378

## Slide 54: Good Engineering Practice (GEP) Stack Height
The EPA has generated formulae for the calculation of the maximum stack height that does not exceed good engineering practice (40 CFR 51.100(ii)) which states that GEP stack height means the greater of:
213 feet, measured from the ground-level elevation at the base of the stack, or
Hg = H + 1.5L
where
Hg = GEP stack height, measured from the ground-level elevation at the base of the stack
H = Height of nearby structure(s) measured from the ground-level elevation at the base of the stack
L = Lesser dimension, height or projected width, of nearby structure(s)

## Slide 55: Ambient Noise
 | Maximum Allowable hourly levels in dB(A) | 
Receptor | Daytime 7:00 – 22:00 | Nighttime 22:00 – 7:00
Residential; institutional; educational | 55 | 45
Industrial; Commercial | 70 | 70

## Slide 56: Electrical capacity
10MW biomass plant
Existing 6MW equipment
  Retro-fit

## Slide 57: Retro-fit
Current rating of equipment may not be up to par for the new source
Equipment include
  Wires
  CT’s
  Switch boxes

## Slide 58: Contingency Incorporation
Penn State OPP policy is to have the allotted demand on the electrical network system
Each point of distribution has a normally open switch and a normally closed switch
This implies even distribution of load across the system

## Slide 59: Incentives
Modified Accelerated Cost-Recovery System (MACRS) & Bonus Depreciation (2008-2012)
  Federal
  Commercial, Industrial, Agricultural
  businesses may recover investments in certain property through depreciation deductions. A number of renewable energy technologies are classified as five-year property
Depreciation Schedule | 
 | Fraction
Year 1 | 0.2000
Year 2 | 0.3200
Year 3 | 0.1920
Year 4 | 0.1152
Year 5 | 0.1152
Year 6 | 0.0576
Year 7 | 0.0000
Year 8 | 0.0000
Year 9 | 0.0000
Year 10 | 0.0000
Year 11 | 0.0000
Year 12 | 0.0000
Year 13 | 0.0000
Year 14 | 0.0000
Year 15 | 0.0000
Year 16 | 0.0000
Year 17 | 0.0000
Year 18 | 0.0000
Year 19 | 0.0000
Year 20 | 0.0000
Total | 1.0000

## Slide 60: Incentives
Renewable Electricity Production Tax Credit (PTC)
  Federal
  Commercial, Industrial
Resource Type | In-Service Deadline | Credit Amount
Wind | December 31, 2012 | 2.2¢/kWh
Closed-Loop Biomass | December 31, 2013 | 2.2¢/kWh
Open-Loop Biomass | December 31, 2013 | 1.1¢/kWh
Geothermal Energy | December 31, 2013 | 2.2¢/kWh
Landfill Gas | December 31, 2013 | 1.1¢/kWh
Municipal Solid Waste | December 31, 2013 | 1.1¢/kWh
Qualified Hydroelectric | December 31, 2013 | 1.1¢/kWh
Marine and Hydrokinetic (150 kW or larger)** | December 31, 2013 | 1.1¢/kWh

## Slide 61
Key Assumptions
based on “overnight” costs
20 year economic life
3 week supply of fuel and consumable materials
Modified Accelerated Cost-Recovery System (MACRS) & Bonus Depreciation
Federal and State Income tax = 36.03%
Yearly inflation rate = 2.1%
No salvage value

## Slide 62: Rate of Return…
Capital costs = $3565/kW=> $35,650,000 for a 10MW plant
  This includes equipment, construction, electrical, fees and contingency costs.
Expenses including fuel = $13,243,524
  This includes labor, maintenance, insurance, ash disposal, management and utility costs.
CO2 capture increases capital costs by 38% bringing it to $4,9197,000 and also increases expenses by 31% totaling $17,349,016.44
Taxes are a combined 36.03% for federal and state
General inflation @ 2.1%

## Slide 63: Capital Cost Details

## Slide 64: Results
Assuming a 20 year life span, the NPV was calculated using
NPV = ∑Cash flows(1+i)N (for N = 1,2,…,20) = $111,586,162
This implies the current Levelized Annual Revenue Requirement is $17,827,169/yr and the Current Levelized Annual Cost of Energy is $0.2394/kWh
The constant Levelized Annual Revenue Requirement is $15,537,106/yr and the constant Levelized Annual Cost of Energy is $0.2087/kWh.

## Slide 65: Sensitivity Analysis
Disruptions in fuel supply, quantity and quality
Technology choice: capital costs, efficiency, operating performance and reliability
Financing terms

## Slide 66
Increase in capital cost increases the current and constant levelized annual cost
Capital Cost |  |  |  |  | 
Case | Relative Change | Capital Cost | LAC Current | LAC Constant | Relative Change in COE
 | (%) | ($) | ($/kWh) | ($/kWh) | (%)
Formula Values |  |  | 0.2394 | 0.2087 | 
-10 | -100 | 0 | 0.1964 | 0.1712 | -18
-9 | -90 | 3,565,000 | 0.2007 | 0.1750 | -16
-8 | -80 | 7,130,000 | 0.2050 | 0.1787 | -14
-7 | -70 | 10,695,000 | 0.2093 | 0.1824 | -13
-6 | -60 | 14,260,000 | 0.2136 | 0.1862 | -11
-5 | -50 | 17,825,000 | 0.2179 | 0.1899 | -9
-4 | -40 | 21,390,000 | 0.2222 | 0.1937 | -7
-3 | -30 | 24,955,000 | 0.2265 | 0.1974 | -5
-2 | -20 | 28,520,000 | 0.2308 | 0.2012 | -4
-1 | -10 | 32,085,000 | 0.2351 | 0.2049 | -2
Base | 0 | 35,650,000 | 0.2394 | 0.2087 | 0
1 | 46 | 52,085,000 | 0.2592 | 0.2259 | 8
2 | 92 | 68,520,000 | 0.2790 | 0.2432 | 17
3 | 138 | 84,955,000 | 0.2989 | 0.2605 | 25
4 | 184 | 101,390,000 | 0.3187 | 0.2777 | 33
5 | 231 | 117,825,000 | 0.3385 | 0.2950 | 41
6 | 277 | 134,260,000 | 0.3583 | 0.3123 | 50
7 | 323 | 150,695,000 | 0.3781 | 0.3295 | 58
8 | 369 | 167,130,000 | 0.3979 | 0.3468 | 66
9 | 415 | 183,565,000 | 0.4177 | 0.3641 | 74
10 | 461 | 200,000,000 | 0.4376 | 0.3814 | 83

## Slide 67
Fuel Cost |  |  |  |  | 
Case | Relative Change | Fuel Cost | LAC Current | LAC Constant | Relative Change in COE
 | (%) | ($/t) | ($/kWh) | ($/kWh) | (%)
Formula Values |  |  | 0.2394 | 0.2087 | 
-10 | -100 | 0.00 | 0.1271 | 0.1108 | -47
-9 | -90 | 16.54 | 0.1383 | 0.1205 | -42
-8 | -80 | 33.07 | 0.1495 | 0.1303 | -38
-7 | -70 | 49.61 | 0.1608 | 0.1401 | -33
-6 | -60 | 66.14 | 0.1720 | 0.1499 | -28
-5 | -50 | 82.68 | 0.1833 | 0.1597 | -23
-4 | -40 | 99.21 | 0.1945 | 0.1695 | -19
-3 | -30 | 115.75 | 0.2057 | 0.1793 | -14
-2 | -20 | 132.28 | 0.2170 | 0.1891 | -9
-1 | -10 | 148.82 | 0.2282 | 0.1989 | -5
Base | 0 | 165.35 | 0.2394 | 0.2087 | 0
1 | -4 | 158.82 | 0.2350 | 0.2048 | -2
2 | -8 | 152.28 | 0.2305 | 0.2009 | -4
3 | -12 | 145.75 | 0.2261 | 0.1971 | -6
4 | -16 | 139.21 | 0.2217 | 0.1932 | -7
5 | -20 | 132.68 | 0.2172 | 0.1893 | -9
6 | -24 | 126.14 | 0.2128 | 0.1854 | -11
7 | -28 | 119.61 | 0.2083 | 0.1816 | -13
8 | -32 | 113.07 | 0.2039 | 0.1777 | -15
9 | -36 | 106.54 | 0.1995 | 0.1738 | -17
10 | -40 | 100.00 | 0.1950 | 0.1700 | -19

## Slide 68
Net Station Efficiency |  |  |  |  | 
Case | Relative Change | Efficiency | LAC Current | LAC Constant | Relative Change in COE
 | (%) | (%) | ($/kWh) | ($/kWh) | (%)
Formula Values |  |  | 0.2394 | 0.2087 | 
-10 | -88 | 5.0 | 1.0258 | 0.8940 | 328
-9 | -79 | 8.5 | 0.6557 | 0.5715 | 174
-8 | -70 | 12.0 | 0.5016 | 0.4371 | 109
-7 | -61 | 15.5 | 0.4170 | 0.3634 | 74
-6 | -53 | 19.0 | 0.3636 | 0.3169 | 52
-5 | -44 | 22.5 | 0.3268 | 0.2848 | 36
-4 | -35 | 26.0 | 0.2999 | 0.2614 | 25
-3 | -26 | 29.5 | 0.2794 | 0.2435 | 17
-2 | -18 | 33.0 | 0.2632 | 0.2294 | 10
-1 | -9 | 36.5 | 0.2502 | 0.2181 | 4
Base | 0 | 40.0 | 0.2394 | 0.2087 | 0
1 | 3 | 41.0 | 0.2367 | 0.2063 | -1
2 | 5 | 42.0 | 0.2341 | 0.2040 | -2
3 | 8 | 43.0 | 0.2316 | 0.2018 | -3
4 | 10 | 44.0 | 0.2292 | 0.1998 | -4
5 | 13 | 45.0 | 0.2269 | 0.1978 | -5
6 | 15 | 46.0 | 0.2248 | 0.1959 | -6
7 | 18 | 47.0 | 0.2227 | 0.1941 | -7
8 | 20 | 48.0 | 0.2207 | 0.1923 | -8
9 | 23 | 49.0 | 0.2188 | 0.1907 | -9
10 | 25 | 50.0 | 0.2170 | 0.1891 | -9

## Slide 69: Conclusion
The LCOE of this biomass plant is about twice the current market price for electricity at 10c/kWh which puts this plant at an economic disadvantage. However, with better incentives and an improvement of some factors such as the net station efficiency, interest rate and debt ratio, the proximity of the LCOE of this plant can be brought closer to the current market cost of electricity.

## Slide 70: References
Power Scorecard. “Electricity from: Biomass” http://www.powerscorecard.org/tech_detail.cfm?resource_id=1
Centre County Comprehensive Plan “Physiographic Regions of Centre County” http://www.co.centre.pa.us/planning/compplan/cc_physiographic.pdf
National Renewable Energy Laboratory “Biomass Maps” http://www.nrel.gov/gis/biomass.html
Centre County Government http://www.co.centre.pa.us/commissioners/abc.asp
Clean Coal Briquette Inc. “Utilization of Biomass” May, 2010.
The California Energy Commission . “Municipal Solid Waste Power Plants” http://www.energy.ca.gov/biomass/msw.html
Techline Forest Products Laboratory “Wood Biomass for Energy” 2004.
Alexandra Dock “Biomass Project” http://www.alexandradockproject.co.uk/biomass-energy/what-is-biomass.aspx
Forced Green. “From Waste to Green Energy Power Plants” http://www.forcedgreen.com/2010/09/from-waste-to-green-energy-power-plants/
“Functioning Principles of a Biomass Combined Heat and Power (CHP) Staion. http://www.unendlich-viel-energie.de/en/biomass/details/article/103/functioning-principles-of-a-biomass-combined-heat-and-power-chp-station.html?&print=1&type=55&no_cache=1
Jeffrey Logan, Stan Mark Kaplan. “Wind Powe r in the United States: Technology, Economic, and Policy Issues” CRS Report for Congress, June 20, 2008.
Michael Schmidt. “Wind Turbine Design Optimization” Strategic Energy Institute
“Wind Electricity Generation”. Practical Action. http://practicalaction.org/docs/technical_information_service/wind_electricity_generation.pdfr
GE Power and Water Renewable Energy. “2.5MW Wind Turbine Series” 2010. http://www.gepower.com/prod_serv/products/wind_turbines/en/2xmw/index.htm
US Department of Energy: Increasing wind energy’s contribution to US electricity supply.
http://energybible.com/wind_energy/wind_speed.html
EIA “Renewable Biomass” http://www.eia.doe.gov/kids/energy.cfm?page=biomass_home-basics-k.cfm
European Biomass Industry Association . http://www.eubia.org/115.0.html
Sakthivale Roshan Dhaneswar Et. Al. “Implementation of Biogas or Biomass at the Pennsylvania State University’s West Campus Steam Plant”, 2010.
The California Energy Commission. “Waste to Energy (WTE) & Biomass in California. http://www.energy.ca.gov/biomass/index.html
Commonwealth of Pennsylvania.. Sandy Ridge Wind Farm Project. , Web. 24 Feb 2011. <http://recovery.pa.gov/portal/server.pt?open=514&objID=525527&mode=2&projectId=DEP35368>.
"Map of Taylor Township, Centre County, Pennsylvania Highlighted." WikiMedia Commons. Web. 24 Feb 2011. http://commons.wikimedia.org/wiki/File:Map_of_Taylor_Township,_Centre_County,_Pennsylvania_Highlighted.png
"Blair County wind projects reach peak." National Wind Watch. National Wind Watch, Inc., 28102010. Web. 24 Feb 2011. <http://www.wind-watch.org/news/2010/10/28/blair-county-wind-projects-reach-peak/>.
Centre County. Recreation & Greenway Plan-Land Resources. , Web. 24 Feb 2011. <http://co.centre.pa.us/gis/greenway_maps/public_lands.pdf>.
United States. Estimates of Windy1 Land Area and Wind Energy Potential by State for Areas >= 30% Capacity Factor at 80m. , Web. 24 Feb 2011. <http://www.windpoweringamerica.gov/pdfs/wind_maps/wind_potential_80m_30percent.pdf>.
"Technologies at work in RansonGreen." Ranson Green . Web. 24 Feb 2011. <http://www.ransongreen.com/Technology.htm>.
United States. Gasification-based Biomass. , Print
Commonwealth of Pennsylvania.. Electric Shopping Guide. , 2011. Print.